## Full System Pop and Avg Day
Full System Average Water Demand Projections Based on Population
Low Projections
Year | Service Area Population (Table 4) | Per Capita Average Day Water Use (Table 11) | Projected Residential Average Day Water Demand (Calculated) | Non-Residential Demands (Table 8 & 16) | Unaccounted for Water (Range from 10% to 7% @ 2020) | Projected Conservation Average Day Total (MGD)
2010 | 246272 | 66 | 16.254 | 9.5 | 2.5754 | 28.3293
2015 | 256584 | 62 | 15.9082 | 10.9 | 2.2787 | 29.0869
2020 | 266896 | 58 | 15.48 | 11.2667 | 1.8723 | 28.6189
2025 | 277208 | 58 | 16.0781 | 11.6333 | 1.9398 | 29.6512
2030 | 287520 | 58 | 16.6762 | 12 | 2.0073 | 30.6835
Median Projections
Year | Service Area Population (Table 4) | Per Capita Average Day Water Use (Table 11) | Projected Residential Average Day Water Demand (Calculated) | Non-Residential Demands (Table 8 & 16) | Unaccounted for Water (Range from 10% to 7% @ 2020) | Projected Median Average Day Total (MGD)
2010 | 246272 | 66 | 16.254 | 9.5 | 2.5754 | 28.3293
2015 | 256584 | 65 | 16.678 | 11.5 | 2.3951 | 30.5731
2020 | 266896 | 64 | 17.0813 | 11.8667 | 2.0264 | 30.9744
2025 | 277208 | 64 | 17.7413 | 12.2333 | 2.0982 | 32.0729
2030 | 287520 | 64 | 18.4013 | 12.6 | 2.1701 | 33.1714
High Projections
Year | Service Area Population (Table 4) | Per Capita Average Day Water Use (Table 11) | Projected Residential Average Day Water Demand (Calculated) | Non-Residential Demands (Table 8 & 16) | Unaccounted for Water (Constant at 10%) | Projected High Average Day Total (MGD)
2010 | 246272 | 66 | 16.254 | 9.5 | 2.5754 | 28.3293
2015 | 256584 | 70 | 17.9609 | 12.1 | 3.0061 | 33.067
2020 | 266896 | 70 | 18.6827 | 12.4667 | 3.1149 | 34.2643
2025 | 277208 | 70 | 19.4046 | 12.8333 | 3.2238 | 35.4617
2030 | 287520 | 70 | 20.1264 | 13.3 | 3.3426 | 36.769
This spreadsheet looks at the water use projections per person. Various rates are considered based on conservation goals. The low projections assume that conservation will meet the stated goal of 58 gallons per person by 2020. The median projection assumes that conservation efforts will reduce average use to 64 gallons per person by 2020. The high projections are based on an assumption that water use remains at 70 gallons per person per day. This spreadsheet can be used to revise population projections and evaluate how that impacts overall projected demand and supply capacity. Conservation goals can also be revised and evaluated. The calculated demands are linked to the other sheets to allow analysis of revisions to projections. Non-residential demands are taken directly from the Black and Veatch memo. Unaccounted for water will trend down from 10% to 7% for the low and median projections and remain constant for the high projections.

## Low Maximum Day by Zone
Low Maximum Day Demand Presented by East Side Zone
Pressure Zone | 2008 AD Demands (Table 13) | Percent of Full System | Percent of Full System on Max Day (Table 15) | 2008 MD Demands (45.06 MGD) | Ratio | Weighted Ratio | Ratio Plus 5% | Ratio Plus 10% | Weighted Percentage | Weighted Average Ratio + 10% | Year | Projected Conservation Average Day Total (MGD) | Using 90th Percentile peaking factor from Table 5 plus 10% (1.830)
1 | 0.37 | 1.4% | 1.2% | 0.54072 | 1.4614 | 0.052349 | 1.5345 | 1.6075 | 3.582% | 0.057584 | 2010 | 28.3293 | 51.8427
2 and 3 | 0.88 | 3.4% | 3.5% | 1.5771 | 1.7922 | 0.18724 | 1.8818 | 1.9714 | 10.45% | 0.20596 | 2015 | 29.0869 | 53.229
5 | 0.03 | 0.1% | 0.1% | 0.04506 | 1.502 | 0.0044836 | 1.5771 | 1.6522 | 0.2985% | 0.0049319 | 2020 | 28.6189 | 52.3726
6E | 6.84 | 26.1% | 28.7% | 12.9322 | 1.8907 | 1.6198 | 1.9852 | 2.0797 | 85.67% | 1.7817 | 2025 | 29.6512 | 54.2617
Total Demand | 8.12 | 31% | 33.5% | 15.0951 |  | 1.8638 |  |  | 100% | 2.0502 | 2030 | 30.6835 | 56.1508
Projected Average Day Demands - Low
Pressure Zone | 2010 | 2015 | 2020 | 2025 | 2030
1 | 0.39661 | 0.40722 | 0.40066 | 0.41512 | 0.42957
2 and 3 | 0.9632 | 0.98895 | 0.97304 | 1.0081 | 1.0432
5 | 0.028329 | 0.029087 | 0.028619 | 0.029651 | 0.030683
6E | 7.394 | 7.5917 | 7.4695 | 7.739 | 8.0084
Total Average Day Demand | 8.7821 | 9.0169 | 8.8719 | 9.1919 | 9.5119
Projected Max Day Demands -Low (Includes a 10% adjustment based on conservation)
Pressure Zone | 2010 | 2015 | 2020 | 2025 | 2030
1 | 0.57961 | 0.62486 | 0.64409 | 0.66732 | 0.69055
2 and 3 | 1.7262 | 1.861 | 1.9182 | 1.9874 | 2.0566
5 | 0.042551 | 0.045873 | 0.047284 | 0.04899 | 0.050695
6E | 13.9796 | 15.0711 | 15.5347 | 16.0951 | 16.6554
Total Max Day Demand | 16.3279 | 17.6028 | 18.1443 | 18.7988 | 19.4533
This spreadsheet looks at the overall low demand projections for the east side assuming that conservation meets current stated goals. The spreadsheets calculates low maximum day based on peaking factors calculated from 2008 demand levels as stated in Table 13 in the Black and Veatch memo. Average day demand projections are taken from the full system population spreadsheet and then calculated for the east side pressure zones. To account for the anticipated increase in peaking factors, the 2015 projections have been increased 5% assuming that we are half way to the conservation goal and 2020 is increased 10% assuming conservation goals have been met.

## Median Maximum Day by Zone
Median Maximum Day Demand Presented by East Side Zone
Pressure Zone | 2008 AD Demands (Table 13) | Percent of Full System | Percent of Full System on Max Day (Table 15) | 2008 MD Demands (45.06 MGD) | Ratio | Weighted Ratio | Ratio Plus 5% | Ratio Plus 10% | Weighted Percentage | Weighted Average Ratio + 10% | Year | Projected Conservation Average Day Total (MGD) | Using 90th Percentile peaking factor from Table 5 plus 10% (1.830)
1 | 0.37 | 1.4% | 1.2% | 0.54072 | 1.4614 | 0.052349 | 1.5345 | 1.6075 | 3.582% | 0.057584 | 2010 | 28.3293 | 51.8427
2 and 3 | 0.88 | 3.4% | 3.5% | 1.5771 | 1.7922 | 0.18724 | 1.8818 | 1.9714 | 10.45% | 0.20596 | 2015 | 30.5731 | 55.9487
5 | 0.03 | 0.1% | 0.1% | 0.04506 | 1.502 | 0.0044836 | 1.5771 | 1.6522 | 0.2985% | 0.0049319 | 2020 | 30.9744 | 56.6831
6E | 6.84 | 26.1% | 28.7% | 12.9322 | 1.8907 | 1.6198 | 1.9852 | 2.0797 | 85.67% | 1.7817 | 2025 | 32.0729 | 58.6934
Total Demand | 8.12 | 31% | 33.5% | 15.0951 |  | 1.8638 |  |  | 100% | 2.0502 | 2030 | 33.1714 | 60.7036
Projected Average Day Demands - Median
Pressure Zone | 2010 | 2015 | 2020 | 2025 | 2030
1 | 0.39661 | 0.42802 | 0.43364 | 0.44902 | 0.4644
2 and 3 | 0.9632 | 1.0395 | 1.0531 | 1.0905 | 1.1278
5 | 0.028329 | 0.030573 | 0.030974 | 0.032073 | 0.033171
6E | 7.394 | 7.9796 | 8.0843 | 8.371 | 8.6577
Total Average Day Demand | 8.7821 | 9.4777 | 9.6021 | 9.9426 | 10.2831
Projected Max Day Demands -Median (Includes a 5% adjustment)
Pressure Zone | 2010 | 2015 | 2020 | 2025 | 2030
1 | 0.57961 | 0.65679 | 0.66541 | 0.68901 | 0.71261
2 and 3 | 1.7262 | 1.9561 | 1.9817 | 2.052 | 2.1223
5 | 0.042551 | 0.048217 | 0.04885 | 0.050582 | 0.052315
6E | 13.9796 | 15.8411 | 16.049 | 16.6182 | 17.1874
Total Max Day Demand | 16.3279 | 18.5022 | 18.7451 | 19.4098 | 20.0746
This spreadsheet looks at the overall median demand projections for the east side assuming that conservation gets to 64 gallons per person per day. The spreadsheets calculates median maximum day based on peaking factors calculated from 2008 demand levels as stated in Table 13 in the Black and Veatch memo. Average day demand projections are taken from the full system population spreadsheet and then calculated for the east side pressure zones. To account for the anticipated increase in peaking factors, the 2015 projections have been increased 5% assuming that we are half way to the conservation goal and 2020 is increased 10% assuming conservation goals have been met.

## High Maximum Day by Zone
High Maximum Day Demand Presented by East Side Zone
Pressure Zone | 2008 AD Demands (Table 13) | Percent of Full System | Percent of Full System on Max Day (Table 15) | 2008 MD Demands (45.06 MGD) | MD:AD Ratio | Weighted Ratio | Ratio Plus 5% | Ratio Plus 10% | Weighted Percentage | Weighted Average Ratio + 10% | Year | Projected Conservation Average Day Total (MGD) | Using 90th Percentile peaking factor from Table 5 plus 10% (1.830)
1 | 0.37 | 1.4% | 1.2% | 0.54072 | 1.4614 | 0.052349 | 1.5345 | 1.6075 | 3.582% | 0.057584 | 2010 | 28.3293 | 51.8427
2 and 3 | 0.88 | 3.4% | 3.5% | 1.5771 | 1.7922 | 0.18724 | 1.8818 | 1.9714 | 10.45% | 0.20596 | 2015 | 33.067 | 60.5126
5 | 0.03 | 0.1% | 0.1% | 0.04506 | 1.502 | 0.0044836 | 1.5771 | 1.6522 | 0.2985% | 0.0049319 | 2020 | 34.2643 | 62.7037
6E | 6.84 | 26.1% | 28.7% | 12.9322 | 1.8907 | 1.6198 | 1.9852 | 2.0797 | 85.67% | 1.7817 | 2025 | 35.4617 | 64.8949
Total Demand | 8.12 | 31% | 33.5% | 15.0951 |  | 1.8638 |  |  | 100% | 2.0502 | 2030 | 36.769 | 67.2873
Projected Average Day Demands - High
Pressure Zone | 2010 | 2015 | 2020 | 2025 | 2030
1 | 0.39661 | 0.46294 | 0.4797 | 0.49646 | 0.51477
2 and 3 | 0.9632 | 1.1243 | 1.165 | 1.2057 | 1.2501
5 | 0.028329 | 0.033067 | 0.034264 | 0.035462 | 0.036769
6E | 7.394 | 8.6305 | 8.943 | 9.2555 | 9.5967
Total Average Day Demand | 8.7821 | 10.2508 | 10.6219 | 10.9931 | 11.3984
Projected Max Day Demands -High (No adjustment included)
Pressure Zone | 2010 | 2015 | 2020 | 2025 | 2030
1 | 0.57961 | 0.67654 | 0.70104 | 0.72553 | 0.75228
2 and 3 | 1.7262 | 2.0149 | 2.0878 | 2.1608 | 2.2405
5 | 0.042551 | 0.049667 | 0.051465 | 0.053263 | 0.055227
6E | 13.9796 | 16.3174 | 16.9083 | 17.4991 | 18.1443
Total Max Day Demand | 16.3279 | 19.0585 | 19.7486 | 20.4387 | 21.1923
This spreadsheet looks at the overall high demand projections for the east side assuming that there is no change in demands. Average use remains constant at 70 gallons per person per day. The spreadsheets calculates high maximum day based on peaking factors calculated from 2008 demand levels as stated in Table 13 in the Black and Veatch memo. Average day demand projections are taken from the full system population spreadsheet and then calculated for the east side pressure zones. Peaking factors remain constant due to no change in rates of conservation.

## Option #1 Average Day
Analysis of Supply Capacity Based on Average Day and Limiting pumping to 12 hours per day
Eastside Water Projections - Average Day Analysis
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
Average Day Water Demand Projections for the East Side |  | 8.7821 | 8.7821 | 8.7821 | 9.0169 | 9.4777 | 10.2508 | 8.8719 | 9.6021 | 10.6219 | 9.1919 | 9.9426 | 10.9931 | 9.5119 | 10.2831 | 11.3984
Percentage of Maximum Day
Max 10-Day Water Demand Projections for the East Side |  | 13.7155 | 13.7155 | 13.7155 | 14.7863 | 15.5419 | 16.0092 | 15.2412 | 15.7458 | 16.5889 | 15.791 | 16.3043 | 17.1685 | 16.3407 | 16.8627 | 17.8015 | 84%
Transfer to Zone 6W1 |  | 0 | 0 | 0 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84
Total Max Day Demand |  | 13.7155 | 13.7155 | 13.7155 | 14.7863 | 16.3819 | 16.8492 | 15.2412 | 16.5858 | 17.4289 | 15.791 | 17.1443 | 18.0085 | 16.3407 | 17.7027 | 18.6415
Well Pumpage Limitation
Pressure Zone | Unit Well | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | 50%
1, 2, & 3 | 25 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
5 | None
6E | 7 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| 8 | [15 empty] | Seasonal Well not Available
| 11 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| 13 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| 15 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| 23 | [15 empty] | Seasonal Well not Available
| 29 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | Well 29 is not limited to lower values
Well 3 Replacement
Well 29 Expansion | [7 empty] | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | Well 29 Expanded to 75% of Well Capacity
East Service Area Total |  | 9 | 9 | 9 | 9 | 9 | 9 | 9.6375 | 9.6375 | 9.6375 | 9.6375 | 9.6375 | 9.6375 | 9.6375 | 9.6375 | 9.6375
East Side Water Supply, Excess Capacity (Deficiency in Red) in MGD on Average Day
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
All Wells on Line |  | 0.2179 | 0.2179 | 0.2179 | -0.016941 | -0.47766 | -1.2508 | 0.76564 | 0.035445 | -0.98444 | 0.44563 | -0.30509 | -1.3556 | 0.12562 | -0.64562 | -1.7609
Only UW 15 Out of service |  | -1.2821 | -1.2821 | -1.2821 | -1.5169 | -1.9777 | -2.7508 | -0.73436 | -1.4646 | -2.4844 | -1.0544 | -1.8051 | -2.8556 | -1.3744 | -2.1456 | -3.2609
This spreadsheet looks at the well pumping capacity for the east side on the average day using the goal of only operating any well 12 hours per day. Since average day demand levels could occur in the early spring and late fall when seasonal wells #8 and #23 are off line, this analysis assumes that they are not available. Demand rates are taken from previous spreadsheets. The analysis is noted at the bottom of the sheet and a capacity of zero or less would indicate that there is not sufficient he capacity in the system to meet the supply criteria for average day. Insufficient capacity is highlighted in red.

## Option #2 Maximum
Analysis of Supply Capacity Based on Maximum Day
Eastside Water Projections - Maximum Day Demand Analysis
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
Average Day Water Demand Projections for the East Side |  | 8.7821 | 8.7821 | 8.7821 | 9.0169 | 9.4777 | 10.2508 | 8.8719 | 9.6021 | 10.6219 | 9.1919 | 9.9426 | 10.9931 | 9.5119 | 10.2831 | 11.3984
Maximum Day Water Demand Projections for the East Side |  | 16.3279 | 16.3279 | 16.3279 | 17.6028 | 18.5022 | 19.0585 | 18.1443 | 18.7451 | 19.7486 | 18.7988 | 19.4098 | 20.4387 | 19.4533 | 20.0746 | 21.1923
Transfer to Zone 6W1 |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1
Total Max Day Demand |  | 16.3279 | 16.3279 | 16.3279 | 17.6028 | 19.5022 | 20.0585 | 18.1443 | 19.7451 | 20.7486 | 18.7988 | 20.4098 | 21.4387 | 19.4533 | 21.0746 | 22.1923
Pressure Zone | Unit Well | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD)
1, 2, & 3 | 25 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
5 | None
6E | 7 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 8 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| 11 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 13 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 15 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 23 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| 29 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Well 3 Replacement
Well 29 Expansion | [7 empty] | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | Well 29 Expanded to 75% of Well Capacity
East Service Area Total |  | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375
East Side Water Supply, Excess Capacity (Deficiency in Red) in MGD on Maximum Day
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
All Wells on Line |  | 3.9721 | 3.9721 | 3.9721 | 2.6972 | 0.7978 | 0.24148 | 2.7932 | 1.1924 | 0.18887 | 2.1387 | 0.52766 | -0.50124 | 1.4842 | -0.13713 | -1.2548
UW 7 & 8 Out off service due to "dirty water" |  | -1.4279 | -1.4279 | -1.4279 | -2.7028 | -4.6022 | -5.1585 | -2.6068 | -4.2076 | -5.2111 | -3.2613 | -4.8723 | -5.9012 | -3.9158 | -5.5371 | -6.6548
Only UW 15 Out of service |  | 0.97206 | 0.97206 | 0.97206 | -0.3028 | -2.2022 | -2.7585 | -0.20681 | -1.8076 | -2.8111 | -0.86128 | -2.4723 | -3.5012 | -1.5158 | -3.1371 | -4.2548
UW 13 & 23 Out of service and UW 25 is down |  | -3.4279 | -3.4279 | -3.4279 | -4.7028 | -6.6022 | -7.1585 | -4.6068 | -6.2076 | -7.2111 | -5.2613 | -6.8723 | -7.9012 | -5.9158 | -7.5371 | -8.6548
This spreadsheet looks at the well pumping capacity for the east side on the maximum day. For reliability and redundancy wells will be considered to be out of service during the maximum day. Demand rates are taken from previous spreadsheets. The analysis is noted at the bottom of the sheet and a capacity of zero or less would indicate that there is not sufficient he capacity in the system to meet the supply criteria for maximum day. Insufficient capacity is highlighted in red.

## Option #3 Max 10 Day
Analysis of Supply Capacity Based on the Maximum 10-Day Demand Projections
Eastside Water Projections - Max 10-Day Analysis
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
Average Day Water Demand Projections for the East Side |  | 8.7821 | 8.7821 | 8.7821 | 9.0169 | 9.4777 | 10.2508 | 8.8719 | 9.6021 | 10.6219 | 9.1919 | 9.9426 | 10.9931 | 9.5119 | 10.2831 | 11.3984
Percentage of Maximum Day
Max 10-Day Water Demand Projections for the East Side |  | 13.7155 | 13.7155 | 13.7155 | 14.7863 | 15.5419 | 16.0092 | 15.2412 | 15.7458 | 16.5889 | 15.791 | 16.3043 | 17.1685 | 16.3407 | 16.8627 | 17.8015 | 84%
Transfer to Zone 6W1 |  | 0 | 0 | 0 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84
Total Max Day Demand |  | 13.7155 | 13.7155 | 13.7155 | 14.7863 | 16.3819 | 16.8492 | 15.2412 | 16.5858 | 17.4289 | 15.791 | 17.1443 | 18.0085 | 16.3407 | 17.7027 | 18.6415
Pressure Zone | Unit Well | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD)
1, 2, & 3 | 25 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
5 | None
6E | 7 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 8 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| 11 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 13 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 15 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 23 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| 29 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Well 3 Replacement
Well 29 Expansion | [7 empty] | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | Well 29 Expanded to 75% of Well Capacity
East Service Area Total |  | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.3 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375 | 20.9375
East Side Water Supply, Excess Capacity (Deficiency in Red) in MGD on Maximum 10-Day Period
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
All Wells on Line |  | 6.5845 | 6.5845 | 6.5845 | 5.5137 | 3.9181 | 3.4508 | 5.6963 | 4.3517 | 3.5086 | 5.1465 | 3.7932 | 2.929 | 4.5968 | 3.2348 | 2.296
UW 7 & 8 Out off service due to "dirty water" |  | 1.1845 | 1.1845 | 1.1845 | 0.11365 | -1.4819 | -1.9492 | 0.29628 | -1.0483 | -1.8914 | -0.25348 | -1.6068 | -2.471 | -0.80324 | -2.1652 | -3.104
Only UW 15 Out of service |  | 3.5845 | 3.5845 | 3.5845 | 2.5137 | 0.91815 | 0.45084 | 2.6963 | 1.3517 | 0.50865 | 2.1465 | 0.79323 | -0.071045 | 1.5968 | 0.23481 | -0.70399
UW 13 & 23 Out of service and UW 25 is down |  | -0.81547 | -0.81547 | -0.81547 | -1.8863 | -3.4819 | -3.9492 | -1.7037 | -3.0483 | -3.8914 | -2.2535 | -3.6068 | -4.471 | -2.8032 | -4.1652 | -5.104
This spreadsheet looks at the well pumping capacity for the east side during the max 10-day demand period. This is considered to be a challenging supply period due to the extended time period. For reliability and redundancy wells will be considered to be out of service during the maximum day. Maximum day demand rates are taken from previous spreadsheets and multiplied by 84% to estimate the maximum 10 day demand. The analysis is noted at the bottom of the sheet and a capacity of zero or less would indicate that there is not sufficient he capacity in the system to meet the supply criteria for the max 10-day demand. Insufficient capacity is highlighted in red.

## Option #4 Max 10 Day at 85%
Analysis of Supply Capacity Based on the Maximum 10-Day Demand Projections and limitiing well operation to 85%
Eastside Water Projections - Max 10-Day Analysis - Running wells only 85% of the time
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
Average Day Water Demand Projections for the East Side |  | 8.7821 | 8.7821 | 8.7821 | 9.0169 | 9.4777 | 10.2508 | 8.8719 | 9.6021 | 10.6219 | 9.1919 | 9.9426 | 10.9931 | 9.5119 | 10.2831 | 11.3984
Percentage of Maximum Day
Max 10-Day Water Demand Projections for the East Side |  | 13.7155 | 13.7155 | 13.7155 | 14.7863 | 15.5419 | 16.0092 | 15.2412 | 15.7458 | 16.5889 | 15.791 | 16.3043 | 17.1685 | 16.3407 | 16.8627 | 17.8015 | 84%
Transfer to Zone 6W1 |  | 0 | 0 | 0 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84 | 0 | 0.84 | 0.84
Total Max Day Demand |  | 13.7155 | 13.7155 | 13.7155 | 14.7863 | 16.3819 | 16.8492 | 15.2412 | 16.5858 | 17.4289 | 15.791 | 17.1443 | 18.0085 | 16.3407 | 17.7027 | 18.6415
Pressure Zone | Unit Well | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD)
1, 2, & 3 | 25 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55
5 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6E | 7 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | Well Pumpage Limitation
| 8 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 2.04 | 0.85
| 11 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55
| 13 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55
| 15 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55
| 23 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19
| 29 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | Well 29 is not limited to lower values
Well 3 Replacement
Well 29 Expansion | [7 empty] | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | 0.6375 | Well 29 Expanded to 75% of Well Capacity
East Service Area Total |  | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 17.48 | 18.1175 | 18.1175 | 18.1175 | 18.1175 | 18.1175 | 18.1175 | 18.1175 | 18.1175 | 18.1175
East Side Water Supply, Excess Capacity (Deficiency in Red) in MGD on Maximum 10-Day Period
Year |  | 2010 |  |  | 2015 |  |  | 2020 |  |  | 2025 |  |  | 2030
|  | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High | Low | Median | High
All Wells on Line |  | 3.7645 | 3.7645 | 3.7645 | 2.6937 | 1.0981 | 0.63084 | 2.8763 | 1.5317 | 0.68865 | 2.3265 | 0.97323 | 0.10895 | 1.7768 | 0.41481 | -0.52399
UW 7 & 8 Out off service due to "dirty water" |  | -0.82547 | -0.82547 | -0.82547 | -1.8963 | -3.4919 | -3.9592 | -1.7137 | -3.0583 | -3.9014 | -2.2635 | -3.6168 | -4.481 | -2.8132 | -4.1752 | -5.114
Only UW 15 Out of service |  | 1.2145 | 1.2145 | 1.2145 | 0.14365 | -1.4519 | -1.9192 | 0.32628 | -1.0183 | -1.8614 | -0.22348 | -1.5768 | -2.441 | -0.77324 | -2.1352 | -3.074
UW 13 & 23 Out of service and UW 25 is down |  | -2.5255 | -2.5255 | -2.5255 | -3.5963 | -5.1919 | -5.6592 | -3.4137 | -4.7583 | -5.6014 | -3.9635 | -5.3168 | -6.181 | -4.5132 | -5.8752 | -6.814
This spreadsheet looks at the well pumping capacity for the east side during the max 10-day demand period. This is considered to be a challenging supply period due to the extended time period. For reliability and redundancy wells will be considered to be out of service during the maximum day. Maximum day demand rates are taken from previous spreadsheets and multiplied by 84% to estimate the maximum 10 day demand. A stated goal is to limit pumping from any well to no more than 85% or 20.4 hours per day. The analysis is noted at the bottom of the sheet and a capacity of zero or less would indicate that there is not sufficient he capacity in the system to meet the supply criteria for the 10 max day with an 85% operating limitation. Insufficient capacity is highlighted in red.

## Peaking Factors from Memo
1.37
1.49
1.52
1.36
1.62
1.62
1.64
1.33
1.67
1.53
1.73
1.51
1.48
1.664 | 90th Percentile
1.632 | 80th Percentile

## LDN Original Spreadsheet
Eastside Water Projections - Black & Veatch Memorandum of January 21, 2011
Water Demand Projections | Year |  | 2010 |  |  | 2015 |  |  | 2030
System-Wide Average Day Water Demand Projections (Note 1)
| Low |  | 31.8 |  |  | 31.9 |  |  | 32
| Mean |  |  | 33.6 |  |  | 34.1 |  |  | 36.1
| High |  |  |  | 35.3 |  |  | 36.2 |  |  | 40.3
East Side Average Day Water Demand Projections. (Note 2)
| Low (Revised) |  | 11.1618 |  |  | 11.1969 |  |  | 11.232
| Mean (Revised) |  |  | 11.7936 |  |  | 11.9691 |  |  | 12.6711
| High (Revised) |  |  |  | 12.3903 |  |  | 12.7062 |  |  | 14.1453
East Side Maximum Day Water Demand Projections. (Note 3)
| Low (Revised) |  | 22.3637 |  |  | 22.4309 |  |  | 22.498
| Mean (Revised) |  |  | 23.573 |  |  | 23.9089 |  |  | 25.2525
| High (Revised) |  |  |  | 24.715 |  |  | 25.3197 |  |  | 28.0741
Available Supply | Zone | Unit Well | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD) | Capacity (MGD)
| 1 | None
| 2 | None
| 3 | 25 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| 4 | 9 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| 5 | None
| 6E | 7 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | 8 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
|  | 11 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | 13 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | 15 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | 23 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
|  | 29 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| East Service Area Total |  | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
Supply Less Demand | East Side Water Supply, Excess Capacity (Deficiency) in MGD
| All Wells on Line |  | 0.43631 | -0.77295 | -1.915 | 0.36913 | -1.1089 | -2.5197 | 0.30195 | -2.4525 | -5.2741
| UW 7 & 8 Out off service due to "dirty water" |  | -4.9637 | -6.173 | -7.315 | -5.0309 | -6.5089 | -7.9197 | -5.098 | -7.8525 | -10.6741
| UW 15 Out of service |  | -2.5637 | -3.773 | -4.915 | -2.6309 | -4.1089 | -5.5197 | -2.698 | -5.4525 | -8.2741
| UW 13 & 23 Out of service and UW 25 is down |  | -6.9637 | -8.173 | -9.315 | -7.0309 | -8.5089 | -9.9197 | -7.098 | -9.8525 | -12.6741
Notes
| Note 1: | B&V Table 16
| Note 2: | Calculated that water consumption for the East Side is 35.1% of the total City using B&V Table 13.
| Note 3: | B&V Peaking Factor of 1.73 times 1.1 to account for additional peaking from conservation
plus 1 MGD pumped to 6W during peak periods.